## BOM
Item ID | Component | System | Description | Quantity | Specification / Rating | Basis | Revision
BOM-001 | Solar PV Array | Solar PV | PV generation source for the conceptual charging-site system | 24 modules (2 strings x 12) | 550 Wp class modules, 13.2 kWp total | Illustrative - see Design_Calculations.xlsx | Original - values added
BOM-002 | PV Combiner / Protection | Solar PV | Conceptual PV combining and protection stage | 1 | 2 string inputs; DC-rated string protection 20 A; DC isolator 40 A | Illustrative - see Design_Calculations.xlsx | Original - values added
BOM-003 | Solar Inverter | Solar PV | Converts the PV electrical output for connection to the AC distribution system | 1 | 12 kW, 3-phase 400 V, MPPT 200-800 V, max DC 1000 V | Illustrative - see Design_Calculations.xlsx | Original - values added
BOM-004 | AC Distribution | EV Charging Site | Conceptual AC distribution interface for BESS and EV charger | 1 | 400 V 3-ph; outgoing devices: inverter 20 A, BESS 16 A, 2 x charger 32 A | Illustrative - see Design_Calculations.xlsx | Original - values added
BOM-005 | BESS (battery modules) | Energy Storage | Stationary battery energy storage system for the conceptual charging site | 6 modules (3S2P) | 5.12 kWh modules; 30.72 kWh nominal, 153.6 V DC nominal | Illustrative - see Design_Calculations.xlsx | Original - values added
BOM-006 | EV Charger | EV Charging | Conceptual AC charging interface between the AC distribution system and the EV (charges via vehicle on-board charger) | 2 | AC Mode 3, 32 A single-phase, 7.36 kW each | Illustrative - see Design_Calculations.xlsx | Revised - AC charger
BOM-007 | EV Battery Pack | EV Battery | Conceptual high-voltage battery pack containing battery modules and associated electrical architecture | 1 | 96S2P, 350 V nominal, 170 Ah, 59.6 kWh nominal | Illustrative - see Design_Calculations.xlsx | Original - values added
BOM-008 | BMS (EV battery) | EV Battery | Battery management and monitoring system for the conceptual EV battery architecture | 1 | TBD | BMS selection out of scope | Corrected - component was mislabeled 'BESS'
BOM-009 | Protection / Contactor (EV battery) | EV Battery | Conceptual high-voltage protection and contactor stage | TBD | Min. 214 A continuous; pack voltage up to 403 V | Illustrative - see Design_Calculations.xlsx | Original - values added
BOM-010 | HV DC Bus | EV Battery | Conceptual high-voltage DC connection within the EV battery electrical architecture | 1 | Peak current about 521 A (150 kW at minimum pack voltage) | Illustrative - see Design_Calculations.xlsx | Original - values added
BOM-011 | Traction Inverter | EV Vehicle | Conceptual power conversion interface between the EV high-voltage system and traction motor | 1 | 150 kW peak (battery side, assumed) | Illustrative - see Design_Calculations.xlsx | Original - values added
BOM-012 | Traction Motor | EV Vehicle | Conceptual electric motor for vehicle traction | 1 | TBD | Sizing out of scope | Original
BOM-013 | 12V / LV System | EV Vehicle | Conceptual low-voltage electrical and vehicle-control support system | 1 | TBD | Out of scope | Original
BOM-014 | BESS PCS | Energy Storage | Power conversion system between BESS DC bus and AC distribution | 1 | 10 kW, 3-phase 400 V, DC window 125-500 V, DC current about 67 A | Illustrative - see Design_Calculations.xlsx | New
BOM-015 | BESS BMS | Energy Storage | Battery management system for stationary BESS modules | 1 | TBD | BMS selection out of scope | New
BOM-016 | On-board Charger (OBC) | EV Vehicle | Converts AC from the charger to DC for the EV battery pack | 1 | 7.4 kW AC input, 92 % efficiency | Illustrative - see Design_Calculations.xlsx | New
BOM-017 | DC-DC Converter (HV to 12 V) | EV Vehicle | Supplies the 12V / LV system from the HV battery | 1 | TBD | Out of scope | New
BOM-018 | Grid Connection and Metering | EV Charging Site | Utility connection, import/export metering and main protection | 1 | TBD | Grid interface not yet drawn | New