## Notes
Solar EV Charging System - Illustrative Design Calculations
Supports the conceptual portfolio design. CONCEPTUAL - NOT A CONSTRUCTION-READY DESIGN.
Purpose | Replaces TBD placeholders with a transparent, formula-driven worked example so the architecture drawings are backed by numbers.
How to use | Change blue cells on the Inputs sheet (yellow = key assumptions). Every other sheet recalculates. Review PASS/FAIL checks.
Colour code | Blue text = input. Black = formula. Yellow fill = key design assumption. Green/red = PASS/FAIL check.
Sheets | Inputs ¦ PV_Sizing ¦ BESS_Sizing ¦ EV_Pack ¦ Cable_Protection ¦ Ref_Tables
Status of values | All module, inverter, battery and cable values are ILLUSTRATIVE. They are not taken from a real datasheet or standard edition and must be replaced with verified data.
Not included | Short-circuit and fault-level studies, protection coordination, earthing design, arc-flash, thermal design, BMS algorithms, grid-connection requirements, and standards compliance.
Grid | A grid-connected 400 V / 50 Hz supply is ASSUMED for the energy balance. The grid interface is not yet on EVD-001 to EVD-010.
Overall check status | ALL CHECKS PASS
Number of checks | 24

## Inputs
Inputs - illustrative example values
Blue = editable input. Yellow fill = key design assumption. All values are ILLUSTRATIVE, not from a real site or datasheet.
Parameter | Description | Value | Unit | Basis / note
1. Site and charging load
v_ll | Site supply, line-to-line | 400 | V | Assumed 3-phase 400 V / 50 Hz grid-connected site (grid interface itself not drawn yet)
v_ph | Site supply, line-to-neutral | 230 | V | Assumed
n_ch | Number of AC charging points | 2 | - | Assumed
i_ch | Rated current per charging point | 32 | A | Assumed Mode 3 AC charger, single-phase
sessions | Charging sessions per day (whole site) | 4 | - | Assumed
e_session | AC energy drawn per session | 20 | kWh | Assumed
solar_share | Target share of daily energy served by PV | 50% | fraction | Design target
bess_share | Share of daily energy served via BESS (evening/night) | 30% | fraction | Design target - energy shifted by storage
2. Solar resource and losses
psh | Peak sun hours (equivalent full-sun hours per day) | 4.5 | h/day | Assumed - replace with site data (e.g. PVGIS / measured)
pr | PV performance ratio | 0.8 | - | Typical planning value
path_eff | Energy path efficiency (PV -> load incl. BESS losses) | 0.95 | - | Assumed blended value
t_min | Minimum site ambient temperature | 10 | degC | Assumed - set from site climate data
t_cell | Maximum PV cell temperature | 70 | degC | Assumed
3. PV module (illustrative 550 Wp class)
p_mod | Module rated power | 550 | Wp | Illustrative - replace with datasheet
voc | Open-circuit voltage Voc (STC) | 49.5 | V | Illustrative
vmp | Voltage at max power Vmp (STC) | 41.5 | V | Illustrative
isc | Short-circuit current Isc (STC) | 14 | A | Illustrative
imp | Current at max power Imp (STC) | 13.26 | A | Illustrative
k_voc | Temperature coefficient of Voc | -0.27 | %/degC | Illustrative
k_vmp | Temperature coefficient of Vmp (approx.) | -0.29 | %/degC | Illustrative
fuse_max | Module max series fuse rating | 25 | A | Illustrative
mod_len | Modules per string | 12 | - | Design choice - checked against inverter window
4. Solar inverter (illustrative 12 kW, 3-phase)
p_inv | Inverter rated AC output | 12 | kW | Illustrative
v_dc_max | Max DC input voltage | 1000 | V | Illustrative
mppt_min | MPPT voltage range - min | 200 | V | Illustrative
mppt_max | MPPT voltage range - max | 800 | V | Illustrative
i_mppt | Max operating DC current per MPPT input | 30 | A | Illustrative
i_isc_max | Max short-circuit current per MPPT input | 40 | A | Illustrative
dcac_min | Acceptable DC/AC ratio - min | 1 | - | Design guideline
dcac_max | Acceptable DC/AC ratio - max | 1.3 | - | Design guideline
5. Stationary BESS (illustrative LFP rack modules)
m_kwh | Battery module nominal energy | 5.12 | kWh | Illustrative (16S x 3.2 V x 100 Ah)
m_v | Battery module nominal voltage | 51.2 | V | Illustrative
m_vmax | Battery module max voltage | 58.4 | V | Illustrative (16 x 3.65 V)
m_vmin | Battery module min voltage | 44.8 | V | Illustrative (16 x 2.8 V)
dod | Usable depth of discharge | 90% | - | Assumed
eta_dis | Discharge efficiency (battery -> AC) | 0.95 | - | Assumed
n_ser | Modules in series per string | 3 | - | Design choice - checked against PCS DC window
pcs_kw | PCS rated power | 10 | kW | Design choice
pcs_eff | PCS efficiency | 0.97 | - | Assumed
pcs_vmin | PCS DC input voltage - min | 125 | V | Illustrative
pcs_vmax | PCS DC input voltage - max | 500 | V | Illustrative
c_max | Max continuous C-rate of module | 0.5 | 1/h | Illustrative
6. EV battery pack and on-board charger (illustrative)
c_v | Cell nominal voltage | 3.65 | V | Illustrative NMC-type cell
c_vmax | Cell max voltage | 4.2 | V | Illustrative
c_vmin | Cell min voltage | 3 | V | Illustrative
c_ah | Cell capacity | 85 | Ah | Illustrative
ns | Cells in series | 96 | - | Design choice (about 350 V class)
np | Cells in parallel | 2 | - | Design choice
soc_win | Usable SOC window | 90% | - | Assumed
pk_kw | Peak traction power (battery side) | 150 | kW | Assumed
ct_kw | Continuous traction power (battery side) | 60 | kW | Assumed
ob_kw | On-board charger rating (AC input) | 7.4 | kW | Assumed
ob_eff | On-board charger efficiency | 0.92 | - | Assumed
7. Cable assumptions
rho | Copper resistivity at operating temperature | 0.0225 | ohm.mm2/m | Approx. value for 70 degC conductor; reactance ignored
d_temp | Derating factor - ambient temperature | 0.87 | - | Assumed ~40 degC ambient (PVC); verify against standard
d_grp | Derating factor - grouping | 0.8 | - | Assumed; verify against standard

## PV_Sizing
Energy demand, PV array and inverter sizing
Illustrative worked example - not a construction design
Parameter | Value | Unit | Formula / note
1. Charging energy demand
Power per charging point | 7.36 | kW | V x I (single-phase)
Peak site charging demand | 14.72 | kW | All points in use at once
Daily charging energy | 80 | kWh/day | Sessions x energy per session
Daily energy to be served from PV (direct + via BESS) | 40 | kWh/day
Daily energy to be served via BESS | 24 | kWh/day
2. PV array sizing
Required PV capacity | 11.6959 | kWp | E / (PSH x PR x path efficiency)
Modules required | 22 | -
Number of strings | 2 | - | Rounded up to whole strings
Installed modules | 24 | -
Installed PV capacity | 13.2 | kWp
Estimated daily PV yield | 47.52 | kWh/day
PV energy reaching load (after path losses) | 45.144 | kWh/day
Estimated daily grid import | 34.856 | kWh/day | Grid interface to be added to drawings
Estimated solar share of charging energy | 56.43% | fraction
Check: installed PV meets required capacity | PASS
3. String voltage and current checks
Module Voc at minimum temperature | 51.5048 | V
Module Vmp at maximum cell temperature | 36.0842 | V
Module Vmp at minimum temperature | 43.3053 | V
String Voc (cold) | 618.057 | V
String Vmp (hot) | 433.011 | V
String Vmp (cold) | 519.663 | V
String Vmp (STC) - reference voltage for cable calcs | 498 | V
Check: string Voc (cold) <= inverter max DC voltage | PASS
Check: string Vmp (hot) >= MPPT minimum | PASS
Check: string Vmp (cold) <= MPPT maximum | PASS
Array Isc (strings paralleled on one MPPT input) | 28 | A
Array Imp (strings paralleled on one MPPT input) | 26.52 | A
Check: array Isc <= MPPT input max Isc | PASS
Check: array Imp <= MPPT input max current | PASS
4. Inverter
DC/AC ratio | 1.1 | -
Check: DC/AC ratio within guideline | PASS
Inverter AC output current | 17.3205 | A | P / (sqrt3 x V)

## BESS_Sizing
Stationary BESS sizing
Illustrative worked example - not a construction design
Parameter | Value | Unit | Formula / note
1. Energy sizing
Energy to be delivered by BESS per day | 24 | kWh/day | From PV_Sizing
Required nominal capacity | 28.0702 | kWh | E / (DoD x discharge efficiency)
Modules required | 6 | -
Parallel strings | 2 | - | Modules per string set on Inputs
Installed modules | 6 | -
Installed nominal capacity | 30.72 | kWh
Usable energy at AC side | 26.2656 | kWh
Check: usable energy >= daily BESS requirement | PASS
2. DC bus and PCS
DC string nominal voltage | 153.6 | V
DC string maximum voltage | 175.2 | V
DC string minimum voltage | 134.4 | V
Check: DC voltage range inside PCS window | PASS
PCS DC current at rated power (nominal voltage) | 67.1177 | A
DC current per parallel string | 33.5588 | A
PCS AC current at rated power | 14.4338 | A | 3-phase
C-rate at rated PCS power | 0.32552 | 1/h
Check: C-rate <= module continuous limit | PASS
Runtime at rated PCS power | 2.6266 | h
PCS power as share of peak charging demand | 67.93% | fraction | Informational - remainder from PV/grid

## EV_Pack
EV battery pack and AC charging session
Illustrative worked example - not a vehicle design
Parameter | Value | Unit | Formula / note
1. Pack configuration
Pack nominal voltage | 350.4 | V
Pack maximum voltage | 403.2 | V
Pack minimum voltage | 288 | V
Pack capacity | 170 | Ah
Pack nominal energy | 59.568 | kWh
Pack usable energy | 53.6112 | kWh
Total cells | 192 | -
2. HV bus currents (for contactor / fuse selection input)
Peak discharge current (worst case at minimum voltage) | 520.8333 | A
Continuous discharge current (nominal voltage) | 171.2329 | A
Peak C-rate | 3.0637 | 1/h
Minimum contactor continuous rating (1.25 x continuous) | 214.0411 | A | Selection margin assumed
3. AC charging session
AC power drawn (limited by charger and on-board charger) | 7.36 | kW
Power into battery | 6.7712 | kW
Energy into battery per session | 18.4 | kWh
Charging time for one session | 2.7174 | h
Charging current into pack (nominal voltage) | 19.3242 | A
SOC added per session (of usable energy) | 34.32% | fraction
Check: pack usable energy >= energy per session | PASS

## Ref_Tables
Reference tables
Indicative values approximating IEC 60364-5-52 / BS 7671 reference method C, PVC-insulated copper, 30 degC ambient. VERIFY against the current standard edition before any real use.
Size (mm2) | Current capacity, 2 loaded conductors (A) - single-phase / DC | Current capacity, 3 loaded conductors (A) - 3-phase | Standard device ratings (A)
1.5 | 19.5 | 17.5 | 6
2.5 | 27 | 24 | 10
4 | 36 | 32 | 16
6 | 46 | 41 | 20
10 | 63 | 57 | 25
16 | 85 | 76 | 32
25 | 112 | 96 | 40
35 | 138 | 119 | 50
50 | 168 | 144 | 63
70 | 213 | 184 | 80
95 | 258 | 223 | 100
120 | 299 | 259 | 125
160
200
250

## Cable_Protection
Cable sizing and protective device selection
Links to Cable_Schedule.xlsx (CBL-xxx). Blue = input. Size = larger of ampacity-based and voltage-drop-based minimum. Reactance and short-circuit withstand are NOT included.
Cable ID | Circuit | Type | Voltage (V) | Design current for protection Ib (A) | Operating current for V-drop (A) | Length one-way (m) | V-drop limit (%) | Protective device In (A) | Derating factor | Min size by ampacity (mm2) | Min size by V-drop (mm2) | Selected size (mm2) | Derated capacity Iz (A) | V-drop (%) | Ib <= In <= Iz | V-drop OK
CBL-001 | PV string -> PV combiner (per string) | DC | 498 | 17.5 | 13.26 | 20 | 1% | 20 | 0.696 | 4 | 2.5 | 4 | 25.056 | 0.5991% | PASS | PASS
CBL-002 | PV combiner -> solar inverter | DC | 498 | 35 | 26.52 | 15 | 1% | 40 | 0.696 | 10 | 4 | 10 | 43.848 | 0.3595% | PASS | PASS
CBL-003 | Solar inverter -> AC distribution | 3ph | 400 | 17.3205 | 17.3205 | 10 | 1% | 20 | 0.696 | 4 | 2.5 | 4 | 22.272 | 0.4219% | PASS | PASS
CBL-004 | AC distribution -> BESS PCS | 3ph | 400 | 14.4338 | 14.4338 | 15 | 1.5% | 16 | 0.696 | 2.5 | 1.5 | 2.5 | 16.704 | 0.8438% | PASS | PASS
CBL-005 | AC distribution -> EV charger (per charger) | 1ph | 230 | 32 | 32 | 30 | 3% | 32 | 0.696 | 6 | 10 | 10 | 43.848 | 1.878% | PASS | PASS
CBL-006 | EV charger -> EV (charging cable) | 1ph | 230 | 32 | 32 | 5 | 1% | 32 | 0.696 | 6 | 4 | 6 | 32.016 | 0.5217% | PASS | PASS
Additional check
String protective device <= module max series fuse rating | [7 empty] | PASS
Notes:
1. Ib for PV circuits = 1.25 x Isc (x number of parallel strings); AC/charger circuits use rated current. Protective device In = next standard rating >= Ib.
2. Voltage drop uses resistance only (copper at operating temperature). Short-circuit withstand, earthing, and fault-loop checks are NOT done.
3. DC protective devices must be DC-rated (e.g. gPV fuses / DC isolators). String-level protection is shown for illustration; whether it is required depends on the standard and the module reverse-current rating.
4. CBL-007 to CBL-010 (EV HV and BMS cables) are vehicle-side and not sized in this workbook.