## Traceability
Requirement ID | Requirement | Design / EVD / Calculation | Verification Method | Verification ID | Verification Status
SYS-001 | The system shall represent the integration of Solar PV generation with the EV charging site. | EVD-001 | Review | VER-001 | Planned
SYS-002 | The system shall represent the conceptual flow of electrical power from Solar PV to the EV charging system. | EVD-001, EVD-002, EVD-003 | Review | VER-002 | Planned
SYS-003 | The system shall include a stationary Battery Energy Storage System (BESS) as part of the charging-site architecture. | EVD-001, EVD-004, EVD-006 | Inspection | VER-003 | Planned
SYS-004 | The EV battery pack shall include battery modules, BMS, protection/contactor stage, HV DC bus, and HV interface. | EVD-007, EVD-008 | Inspection | VER-004 | Planned
SYS-005 | The EV battery architecture shall represent the BMS monitoring and control relationship with the battery system. | EVD-008 | Review | VER-005 | Planned
SYS-006 | The vehicle architecture shall distinguish the high-voltage power system from the 12V/LV control system. | EVD-009 | Review | VER-006 | Planned
SYS-007 | The project shall maintain organized CAD drawings and engineering documentation for portfolio demonstration. | EVD-001 to EVD-010 | Inspection | VER-007 | Planned
SYS-008 | The site shall provide 2 AC charging points, each rated 32 A single-phase (7.36 kW), for a peak charging demand of 14.7 kW (illustrative design basis). | EVD-004, EVD-005; Design_Calculations.xlsx (Inputs) | Inspection | VER-008 | Planned
SYS-009 | The PV array shall have an installed capacity of at least 11.7 kWp to serve 50 % of an 80 kWh/day charging demand (illustrative design: 13.2 kWp, 24 modules). | EVD-002, EVD-003; Design_Calculations.xlsx (PV_Sizing) | Analysis | VER-009 | Complete (illustrative)
SYS-010 | String open-circuit voltage at the minimum site temperature shall not exceed the inverter maximum DC voltage, and string Vmp shall stay within the MPPT window (illustrative: 618 V vs 1000 V). | EVD-003; Design_Calculations.xlsx (PV_Sizing) | Analysis | VER-010 | Complete (illustrative)
SYS-011 | The BESS shall deliver at least 24 kWh of usable energy per day with a 10 kW PCS (illustrative design: 30.7 kWh nominal, 26.3 kWh usable). | EVD-006; Design_Calculations.xlsx (BESS_Sizing) | Analysis | VER-011 | Complete (illustrative)
SYS-012 | Each sized cable shall be protected by a device with design current Ib <= device rating In <= derated cable capacity Iz. | EVD-010; Cable_Schedule.xlsx; Design_Calculations.xlsx (Cable_Protection) | Analysis | VER-012 | Complete (illustrative)
SYS-013 | Voltage drop on each sized cable shall not exceed its circuit limit (1 % to 3 %). | EVD-010; Cable_Schedule.xlsx; Design_Calculations.xlsx (Cable_Protection) | Analysis | VER-013 | Complete (illustrative)
SYS-014 | The EV pack usable energy shall exceed the energy delivered per charging session (illustrative: 53.6 kWh vs 18.4 kWh). | EVD-007; Design_Calculations.xlsx (EV_Pack) | Analysis | VER-014 | Complete (illustrative)