## Verification_Plan
Verification ID | Requirement ID | Verification Method | Verification Activity | Expected Result | Status
VER-001 | SYS-001 | Review | Review EVD-001 system architecture for Solar PV and EV charging site integration. | Solar PV generation and EV charging site integration is represented. | Planned
VER-002 | SYS-002 | Review | Review EVD-001, EVD-002, and EVD-003 for the conceptual electrical power flow from Solar PV to the EV charging system. | Conceptual electrical power flow is clearly represented. | Planned
VER-003 | SYS-003 | Inspection | Inspect EVD-001, EVD-004, and EVD-006 for the stationary BESS representation. | Stationary BESS is included in the charging-site architecture. | Planned
VER-004 | SYS-004 | Inspection | Inspect EVD-007 and EVD-008 for battery modules, BMS, protection/contactor stage, HV DC bus, and HV interface. | All required EV battery architecture elements are represented. | Planned
VER-005 | SYS-005 | Review | Review EVD-008 for the BMS monitoring and control relationship with the battery system. | BMS monitoring and control relationship is clearly represented. | Planned
VER-006 | SYS-006 | Review | Review EVD-009 for separation of the high-voltage power system and the 12V/LV control system. | HV power and 12V/LV control systems are clearly distinguished. | Planned
VER-007 | SYS-007 | Inspection | Inspect the project folder structure, CAD drawings, and engineering documentation for organization and completeness. | CAD drawings and engineering documentation are organized for portfolio demonstration. | Planned
VER-008 | SYS-008 | Inspection | Inspect EVD-004 and EVD-005 for two AC charging points and compare with the Inputs sheet. | Two 32 A single-phase charging points are shown and match the calculation basis. | Planned
VER-009 | SYS-009 | Analysis | Run Design_Calculations.xlsx, sheet PV_Sizing: compare installed kWp with required kWp. | Installed PV capacity is greater than or equal to required capacity (check = PASS). | Complete (illustrative)
VER-010 | SYS-010 | Analysis | Run PV_Sizing string checks: Voc at minimum temperature, Vmp hot and cold, Isc and Imp per MPPT input. | All string voltage and current checks = PASS. | Complete (illustrative)
VER-011 | SYS-011 | Analysis | Run BESS_Sizing: compare usable energy with the daily BESS requirement; check PCS DC window and C-rate. | Usable energy meets the requirement; all BESS checks = PASS. | Complete (illustrative)
VER-012 | SYS-012 | Analysis | Run Cable_Protection: check Ib <= In <= Iz for every circuit. | All circuits = PASS. | Complete (illustrative)
VER-013 | SYS-013 | Analysis | Run Cable_Protection: check voltage drop against the limit for every circuit. | All circuits = PASS. | Complete (illustrative)
VER-014 | SYS-014 | Analysis | Run EV_Pack: compare usable pack energy with energy delivered per session. | Pack usable energy exceeds session energy (check = PASS). | Complete (illustrative)